## Slide 1: IT Infrastructure Architecture
Datacenters
(chapter 7)
Infrastructure Building Blocks
and Concepts

## Slide 2: Introduction
Most IT infrastructure hardware, except for end user devices, are hosted in datacenters
A datacenter provides:
  Power supply
  Cooling
  Fire prevention and detection
  Equipment racks

## Slide 3: History
Early datacenters (computer rooms) were designed and built for large mainframe systems
A mainframe, together with its peripheral systems easily filled up a large computer room

## Slide 4: Today’s datacenters
Today’s datacenters are equipped with standardized 19" racks
  They house servers, storage devices, and network equipment
  They are installed in rows forming corridors between them
Very large datacenters today contain shipping containers packed with thousands of servers each
  When repairs or upgrades are needed, entire containers are replaced

## Slide 5: Datacenter building blocks

## Slide 6: Datacenter categories
Typical datacenter categories:
  Sub Equipment Room (SER) – a SER is also known as a patch closet
  Main Equipment Room (MER) – a MER is a small datacenter in the organization’s subsidiaries or buildings
  Organization owned datacenter – a datacenter that contains all central IT equipment for the organization
  Multi-tenant datacenter – used by service providers that provide services for multiple other organizations. These datacenters are typically the largest

## Slide 7: Datacenter location
Many variables should be considered to determine where a datacenter could be installed
Examples:
  Environment of the datacenter
  Visibility of the datacenter
  Utilities available to the datacenter
  Datacenters located in foreign countries

## Slide 8: Physical structure
The physical structure of a datacenter includes components that need special attention:
  Floors
  Walls
  Windows
  Doors
  Water and gas pipes

## Slide 9: Floors
In a typical datacenter, the floor must be able to carry 1500 to 2000 kg/m2
  One fully filled 19” computer rack weighs up to 700 kg
  The footprint of a rack is about 60x100 cm, leading to a floor load of 1166 kg/m2
  In office buildings typically the floor can carry approximately 500 kg/m2

## Slide 10: Floors
Raised floors consist of a metal framework carrying removable floor tiles
Tiles are usually 60×60 cm
Tiles can be lifted individually to reach cables installed under the raised floor
Vents provide cool air flow to the racks placed on the floor
Under the raised floor, data and power cables are installed
  As alternative, overhead cable trays can be used

## Slide 11: Floors
Raised floors have the following disadvantages:
  They are expensive
  The total available height in the datacenter is decreased
  The maximum floor load is limited
  Doors and equipment loading slopes are hard to install due to the difference in floor height
  Under the raised floor, a fire could easily spread through the entire datacenter

## Slide 12: Walls, windows, and doors
Walls should reach from the floor to the building’s ceiling
  Because of fire safety and physical intrusion prevention
  Adequate fire rating is needed to serve as a physical firewall
Windows are not desirable in a datacenter
Windows must be:
  Translucent
  Shatterproof
  Impossible to open
Doors should be large enough to have equipment brought in
Doors must resist forced entry

## Slide 13: Water and gas pipes
Water or gas pipes may have been installed:
  Under the floor
  In the walls
  Above the ceiling of the datacenter
Leakage from water pipes in the ceiling of a datacenter could lead to damage of equipment
Datacenter operators should know where the shutoff valves are

## Slide 14: Datacenter layout

## Slide 15: Power supply
Energy usage is a key issue for datacenters
Power drawn by datacenters:
  A few kilowatts (kW) for one rack of servers
  Dozens of megawatts (MW) for large facilities
The amount of power available in a datacenter is expressed as the number of kilowatts per m2
  Known as power density
Normal-density datacentre: between 2 to 6 kW/m2
High-density datacentre: between 10 and 20 kW/m2

## Slide 16: Power supply
Example:
  If a HP DL380 server uses 250W power
  A rack could physically hold 40 servers
  Available energy density is 2 to 6 kW/m2
  Only between 8 and 24 servers can be placed in the rack
In practice most server racks cannot be fully equipped
A high-density datacentre allows racks to be filled with approximately 40 to 80 servers

## Slide 17: Uninterruptable Power Supply (UPS)
Power issues can occur in the utility power supply
Possibly leading to:
  Downtime
  Damage to equipment
Types of power issues:
  Blackout
  Surge
  Spike
  Brownout
  Waveform issues
An Uninterruptable Power Supply (UPS):
  Is independent of the utility power supply
  Provides high quality electrical power

## Slide 18: Uninterruptable Power Supply (UPS)
A UPS installation consists of:
  Filters
  A diesel power generator
  A set of batteries or a flywheel system

## Slide 19: Uninterruptable Power Supply (UPS)
Battery powered UPSs:
  Standby UPS systems (also known as off-line systems)
    Used in small setups (a few workstations or servers)
  Line interactive UPS systems
    Use a transformer between the utility power and the IT equipment
    Works as a filter for many of the power issues
  Double conversion UPS systems
    Convert the AC utility power to DC power and then back to high quality AC power

## Slide 20: Power distribution
A power distribution unit (PDU) is a device with multiple power outlets
  Distributes power to equipment located in the datacenter
Two types of PDUs:
  Large floor mounted PDUs take main feeds (usually 3 phase power) and distribute it into multiple smaller feeds to computer racks
  Power Strips that feed equipment in racks
Most Infrastructure components can be equipped with two power supplies for redundancy
For availability reasons at least two power strips are needed to power equipment in a rack
  Each feeds one of the two power supplies in the equipment

## Slide 21: Uninterruptable Power Supply (UPS)
Two independent power feeds to racks
UPS should not be a Single Point of Failure

## Slide 22: Cooling
> 90% of all power used by IT infrastructure components is converted into heat
All heat has to be dissipated by a cooling system
Two types of cooling systems:
  Computer Room Air Conditioners (CRAC)
    Refrigerant-based units connected to outside condensing units
  Computer Room Air Handlers (CRAH)
    Chilled water based and connected to outside chillers
    A chiller produces chilled water via a refrigeration process

## Slide 23: Cooling
The efficiency of a cooling system is specified in:
  EER - Energy Efficiency Ratio
    The measure of efficiency at maximum air conditioning load
    The ratio between output cooling in BTU per hour and the electric energy input in Watts at a given operating point
  SEER - Seasonal Energy Efficiency Ratio
    Same as EER, but seasonal data is used for the measurement
    The time of year the cooling system is used most (typically in the summer)
  COP - Coefficient Of Performance
    The ratio between cooling load in kW and the electric energy input in kW
    Normal values are between 3 and 10

## Slide 24: Operating temperatures
Infrastructure components have maximum operating temperatures
  Servers shut themselves down at an air inlet temperature of 40 degrees Celsius
The air temperature in the datacenter usually ranges from 18 degrees to 27 degrees Celsius
Using higher temperatures saves cooling capacity and power
  Raising the temperature in a datacenter with one degree Celsius lowers the cost for cooling by approximately 5%

## Slide 25: Airflow

## Slide 26: Humidity and dust
The humidity of the air in a datacenter is critical for the IT infrastructure components
  Air humidity should between 40% and 60%
The number of dust particles in a datacenter should be minimized
  Don’t allow visitors in the datacenter
  People should wear dust-free clothing (like white coats) and protective sleeves around their shoes

## Slide 27: Fire prevention, detection, and suppression
Fire is one of the main enemies of a datacenter
  A short circuit in a cable
  Defect equipment
Fires can spread around very quickly
  Because of the air flow in the datacenter and the frequent use of raised floors
Smoke could damage equipment in the datacenter
  Even if a fire starts outside of the datacenter’s computer room

## Slide 28: Fire prevention, detection, and suppression
Suppressing fire in a datacenter consists of four levels:
  Fire prevention – Avoid a fire
  Passive fire protection – Limit the exposure of the fire once it has started
  Fire detection systems – Detect smoke and fire
  Fire suppression systems – Extinguish the fire once it is detected

## Slide 29: Equipment racks
A 19” rack is a standardized metal enclosure to house IT infrastructure components
The height of a rack is measured in rack unit or 'U‘
  One U is 44.5 mm
A typical rack is 42U high

## Slide 30: Datacenter energy efficiency
IT accounts for approximately 2% of all the world’s CO2 emissions
During the lifetime of a server the amount of money spent on electricity can be much higher than the cost of the server itself
The datacenter itself uses power as well
  Cooling system
  Lighting
  Heating of the operator rooms
  Etc.

## Slide 31: Datacenter energy efficiency
The Power Usage Effectiveness (PUE) metric measures the power used by the datacenter
The PUE is calculated by dividing the amount of power used by the datacenter, by the power used to run the IT equipment in it
Typical PUE value of a datacenter is between 1.1 and 2.0
  Running a datacenter with a PUE of 1.5 means that for each watt of power used by the IT equipment an extra half watt is used by the rest of the datacenter

## Slide 32: Datacenter availability

## Slide 33: Availability tiers

## Slide 34: Availability tiers

## Slide 35: Availability tiers
The tier classification only describes the availability of the datacenter facilities
  Not the availability of the IT infrastructure components
A tier 3 datacenter running an IT infrastructure with an availability of 99.990% will have a total availability of

## Slide 36: Redundant datacenters
Multiple redundant datacenters can be used to increase availability
Multiple datacenters are a must when higher availability than 99.995% is needed
  If a datacenter with all its equipment has an availability lower than tier 1, two datacenters can reach an availability of the same level as one tier 4 datacenter
Redundant datacenters should be at least 5 km apart
  Based on the effect of incidents like the 9/11 terrorist attacks in the USA and reports of explosions in factory plants and fireworks storage

## Slide 37: Datacenter performance

## Slide 38: Datacenter performance
The datacenter itself does not provide performance to IT Infrastructures, except for the bandwidth of the internet connectivity and the scalability of the location

## Slide 39: Datacenter security

## Slide 40: Physical security
Ensure that equipment is physically safe behind the datacenter doors
Physical access to the datacenter must be restricted to selected and qualified staff
An entry registration system should be used
A log should be maintained containing all staff entering and leaving the datacenter
Doors must be secured using conventional locks (for instance for dock loading doors) or electronic locks
  Electronic locks should open only after proper authentication

## Slide 41: Physical security
Entry points can be implemented as:
  Regular doors
  Mantraps
    Staff is routed through a set of double doors that may be monitored by a guard
  Revolving doors
    Only one person at a time can enter the datacenter’s restricted area
Entries can be equipped with weighing scales to ensure only one person enters the restricted area